## Schedule 1
To be Competed by the Developer & TIC Section of SDCC and forwarded to Irish Water with recommendations of whether estate is Category A or B, along with the Schedule 2 form which the Water Services Section completed following their assessment of the Water Services infrastructure | [6 empty] | The following is checked from data/details received on TIC application: (NB: In the case of a request from the majority of the residents under Section 180, it is unlikely that the following data/detail will be available to the Planning Authority)
| Completion Colour Code: | Developer |  |  | SDCC TIC Section
| Planning Authority: |  | South Dublin County Council |  |  |  |  | Application received from:
[8 empty] | Developer: | Yes |  | No
| Developer Name: | [6 empty] | Majority of residents: | Yes |  | No
| Name of Development/Housing Estate: | [6 empty] | Date of receipt of application:
| Location of Development: | [6 empty] | As Constructed Site Layout: | Yes |  | No
| Parent Planning Reference No: | [6 empty] | As Constructed Plan & Section Watermain: | Yes |  | No
| Map Outlining proposed area to be | [6 empty] | As Constructed Plan & Section Sewers: | Yes |  | No
considered for TIC including all relevant
| Planning Permission references: |  | Attached – | Yes |  | No |  | Surveys Wastewater Network: | Yes |  | No
| Site Location Map: |  | Attached – | Yes |  | No
| Site Layout: |  | Attached – | Yes |  | No |  | Surveys Water Network: | Yes |  | No
| Number of Houses Constructed: | [6 empty] | Test Certificates: | Yes |  | No
| Geo References ( Site Centroid): | [6 empty] | Wayleaves: | Yes |  | No
| Length of Roadway ( if available): | [6 empty] | Engineer/Architects Certificates: | Yes |  | No
| Is there a current Bond in Place: |  |  | Yes |  | No |  | Overall comments:
If Yes:
Value of the Bond:
Planning recommendation to be completed after return of Schedule 2
| Phase of Bond if relevant: | [6 empty] | Planning Recommendation:
[8 empty] | Development Category (reference Section 4 of MoU) |  | Category A
| Bond type, Cash/Insurance/Other: | [8 empty] | Category B
| Expiry Date of Bond Claims: | [6 empty] | Financing Option (reference Section 7 of MoU) |  | Option 1
Option 2
| Name of Financial Institution: | [8 empty] | Option 3
Comment if applicable:
Signed:
| Is Enforcement Action an option? |  |  | Yes |  | No
Title:
Comments as applicable:
Date:
Note on F22: Padhraic McGillycuddy: Source Irish Grid Ref Finder
Note on B42: Enforcement is always an option unless 12 years has passed since Planning Permission was granted

## Schedule 2 - Inspection Form
To be completed jointly by the Developer & SDCC Water Services - This inspection form is to assess condition and compliance with standards of water services assets for the transfer of assets to Irish Water on conclusion of the taking in charge process. It is a visual survey and unless otherwise indicated no testing of the infrastructure was undertaken.
Completion Colour Code: |  |  | Developer |  |  | SDCC Water Services Section
| Planning Authority: |  |  | South Dublin County Council
| Planning Ref. No(s) |  |  | SD
Number of Units:
Development Name:
Address:
Name of Developer:
Agent ( if applicable):
| Date of Inspection: |  |  | Initial: |  |  | Follow up:
The table hereunder is a checklist to be utilised to assist in the site inspection and is a measure of the information on water services assets required by Irish Water.
| Engineers and Architects Certificates |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
Copies of submitted certificates
Copies of submitted reports
| As Constructed Drawings |  |  | Available |  |  | Number
|  |  |  | Yes | No | N/A
Electronic copy submitted
Hard Copies
| Site Layout Drawings |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
Indicate extent of roads and lands to be taken in charge
Indicates House Numbers where applicable
Details pre-existing topography, services, water courses etc.
Existing wayleaves or other burdens on lands
| Watermains |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
| Plan of watermain | [5 empty] | Developer to provide dwg to WS
| Locations of all sluice valves, scour valves, air valves, hydrants, meters, water service control units are clearly indicated | [5 empty] | Developer to provide dwg to WS
Route, diameter and class of water pipelines indicated
Indicate details of bulk meter type (electronic or mechanical) and bypass arrangements if applicable
Inspect depth of water services for adequacy of cover
| Foul Sewers |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
Plan of sewers
Longitudinal sections showing gradient of pipeline, pipe diameter and pipe type
Location of manholes including finished ground/cover level and invert level are identified on plan
Comment on the grade, standard and condition of all covers and frames
Indicate location and route of all connections from sewers to individual properties
| Test Certificates |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
Water pipelines - pressure tests (at 1.5 times working pressure)
Water Losses (minimum night flow should not exceed 6l/dwelling/hour)
Sewer pipelines - Air tests to BE EN 1610
| Surveys Water Network |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
All valves and hydrants to be opened and checked for compliance with standards and dipped to crown of pipe to ascertain adequacy of cover.
1:10 stop valves to be opened and checked for compliance with specification and depth of cover.
| Surveys Wastewater Network |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
CCTV Survey-with reports including classification of all defects and defect grading.
Manhole Survey–visual check on benching, infiltration, cover and biscuit integrity and flushness with surface, accessibility, subsidence, cracking, ponding.
Dye tests- 1 in 10 premises to be subject to dye test
Infiltration test- Guideline: Infiltration shall not exceed 0.5 litres/linear metre of pipeline/metre nominal bores over a period of 30 minutes.
| Surveys Surface Water Network |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
Random check of manholes for presence of foul sewage. (1/10).
| Wayleaves and Easements |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
Copies of all wayleaves, burdens, land transfers and other document pertinent to development to be submitted.
| Service History |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
Detail significant watermain leaks / bursts / issues
Detail significant sewer blockages / bursts / issues
Flooding risk or potential
| Pumping Stations |  |  | Available |  |  | Comment
|  |  |  | Yes | No | N/A
Water Pumping Station
Wastewater Pumping Station
As constructed drawings and specifications to include type and size of pumps; wiring diagrams for control panel and switch gear; telemetry system; lifting equipment including certification of same.
Reports associated with supervision of installation
Operational Arrangements (Council/Developer/Service Contract)
Performance issues-Where Council have intervened
MPRN and Account Holder Details from electricity account
Actual or estimated annual consumption from Electricity bill.
| Sketches Attached ( optional): |  |  | Yes |  |  |  | No
Conclusion:
Recommended time frame for execution of water service remedial works:
Anticipated costs for remedial works to water service infrastructure:
Proceed to take in charge:
or
Works required prior to taking in charge:
| Signed: | [5 empty] | By Senior Engineer, Water Services
| Grade: | Senior Engineer, SDCC WS
Date:
Note: Please attach copies of all reports, drawings, surveys etc with completed forms.
Note on A71: WS/Drainage
Note on A72: WS/Drainage
Note on A75: WS/Mechanical Section
Note on A76: WS/Mechanical Section
Note on A77: WS/Mechanical Section
Note on A78: WS/Mechanical Section
Note on A79: WS/Mechanical Section
Note on A80: WS/Mechanical Section
Note on A81: WS/Mechanical Section
Note on A82: WS/Mechanical Section